## General
SunEnergy Power International
Site Assessment Workbook
Input Information
2008-09-20
Facility Name | PIH - Boucancarre
General Site Information
Item | Input | Remarks
Date of Audit | 2008-11-10
Name of Auditor | Walt Ratterman
Affiliation of Auditor
Contact Person at Site:
Phone Number of Contact Person at Site:
Title of Contact Person
Department | Central
Type of Facility | Small to Medium Health Center | Health Center, Hospital, etc.
Number of Patients per day
Describe Facility |  | e.g. Lab, computer center, etc…
For Labs: Is this a Basic, Palliative Care, or ARV lab?
Does this facility have a server?
Operating Hours of Facility:
Operating Days of Facility:
Are there air conditioners in use in this facility, or planned to be in use? | 1 in Lab, Pharmacy Depot, and OR | If so, please be sure to include them with on the appropriate load sheet.

## Site Power
SunEnergy Power International
Site Assessment Workbook
Input Information
2008-09-20
Facility Name | PIH - Boucancarre
Site Power Supplies
Item | Input | Remarks
EDH
Is the site connected to EDH?
If YES, describe when EDH is usually on between the hours of 0700 and 1900 hrs.
If Yes, describe when EDH is usually on between the hours of 1900 and 0700 hours.
Add any comments regarding the power availability of EDH, power quality of EDH, or any other observations.
DELCO / GENERATOR
Is the generator for the entire facility, or dedicated to these loads?
From Generator Nameplate:
Manufacturer and Model No. | CAT-GEP-30SP-3
Provide Data for Continuous Power Ratings:
KVA | 35
KW | 35
Power Factor | 1
Voltage and Phase | 120/240 single phase
| 145 A / leg | 150A Total, on two legs
Overall Condition and age of Generator | good
Is it connected 1-Phase or 3-Phase | single phase
How many hours/day does it run? | 10 Hours
How much fuel per hour or per day does it consume? | 20 GPD
Provide Photos of Generator

## Inv-Batty Equip
SunEnergy Power International
Site Assessment Workbook
Input Information
2008-09-20
Facility Name | PIH - Boucancarre
Existing Inverter - Battery Equipment (with no PV system)
Item | Input | Remarks
Existing Inverter(s)
Manufacturer and Catalog No. | 3 DR under stairs, 1 Magnum by X-Ray, 1 DR in Bank, 1 DR in Internet Café | If more than one inverter, use supplemental pages.
Wattage | varies
Voltage | 24
Condition | poor
Describe Installation. | poor
Provide PHOTO of the Inverter.
Existing Batteries:
Manufacturer and Catalog No. | T-105
Number of Batteries | 60 Total batteries in all locations.
Are the batteries inside the building or outside of the building? | inside
Are the batteries in a cage? | no
Is the cage Locked?
Condition of the Batteries:
Provide PHOTO of the Batteries
System Operation
How many hours does the system operate when there is no EDH and no Generator input? | Inverters seem to last only 3 or 4 hours - comment is too many fans.

## Boucancarre - to SW
SunEnergy Power International
Site Assessment Workbook
Input Information
2009-01-09
Facility Name |  | PIH - Boucancarre
Existing Loads
|  |  |  | No Contact |  | Contact |  | No Contact |  | Contact
Area | QTY | Load | Watts | Loads |  | Loads |  | WHRS | WHRS | WHRS | WHRS | Watthrs | Total | Days | Wkly
|  |  | Each | Run | Not | Run | Not | Run | Not | Run | Not | Total | Conn | Per Wk | Calc
Watts
Laboratory | 4 | Microscopes | 50 |  |  | 3 | 3 | 0 | 0 | 600 | 600 | 1200 | 200
| 2 | Centrifuge | 200 |  |  | 2 | 2 | 0 | 0 | 800 | 800 | 1600 | 400
| 1 | Computer | 150 |  |  | 4 | 4 | 0 | 0 | 600 | 600 | 1200 | 150
| 1 | Refrigerator - Elec | 50 |  |  | 4 | 20 | 0 | 0 | 200 | 1000 | 1200 | 50
| 1 | Refrigerator - Gas | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1 | UV Light | 75 |  |  | 4 | 6 | 0 | 0 | 300 | 450 | 750 | 75
| 2 | Light | 20 |  |  | 4 | 6 | 0 | 0 | 160 | 240 | 400 | 40
| 1 | Fan | 75 |  |  | 4 | 6 | 0 | 0 | 300 | 450 | 750 | 75
| 1 | Point Care | 300 | 3 | 3 |  |  | 900 | 900 | 0 | 0 | 1800 | 300
| 1 | Sysmex | 200 | 2 | 1 |  |  | 400 | 200 | 0 | 0 | 600 | 200
| 1 | Reflotron | 70 | 2 | 1 |  |  | 140 | 70 | 0 | 0 | 210 | 70
[10 empty] | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Main Building | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Operating Room | 1 | Anisthesiology Machine | 600 |  |  | 2 | 1 | 0 | 0 | 1200 | 600 | 1800 | 600
| 1 | Vacuum Machine | 200 |  |  | 2 | 1 | 0 | 0 | 400 | 200 | 600 | 200
| 1 | Autoclave | 1350 |  |  | 2 |  | 0 | 0 | 2700 | 0 | 2700 | 1350
| 1 | Other Equipment | 1000 |  |  | 2 |  | 0 | 0 | 2000 | 0 | 2000 | 1000
| 1 | Surgical Light | 150 |  |  | 2 | 1 | 0 | 0 | 300 | 150 | 450 | 150
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Maternity | 1 | UV Light | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 1 | Fans | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 1 | X-Ray Viewing | 50 |  |  | 1 | 1 | 0 | 0 | 50 | 50 | 100 | 50
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Pharmacy Depot | 2 | Lights | 20 |  |  | 4 | 4 | 0 | 0 | 160 | 160 | 320 | 40
| 3 | Fans | 75 |  |  | 4 | 4 | 0 | 0 | 900 | 900 | 1800 | 225
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Consultation Rooms | 4 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 1200 | 1200 | 2400 | 300
| 4 | Lights | 20 |  |  | 4 | 4 | 0 | 0 | 320 | 320 | 640 | 80
| 4 | Computers | 75 |  |  | 4 | 4 | 0 | 0 | 1200 | 1200 | 2400 | 300
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Large Waiting Area | 2 | UV Light | 75 |  |  | 4 | 4 | 0 | 0 | 600 | 600 | 1200 | 150
| 4 | Fans | 100 |  |  | 4 | 4 | 0 | 0 | 1600 | 1600 | 3200 | 400
| 1 | TV | 150 |  |  | 4 |  | 0 | 0 | 600 | 0 | 600 | 150
| 6 | Lights | 20 |  |  | 2 |  | 0 | 0 | 240 | 0 | 240 | 120
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Salle A Ward | 2 | UV Light | 75 |  |  | 4 | 4 | 0 | 0 | 600 | 600 | 1200 | 150
| 2 | Fans | 75 |  |  | 4 | 4 | 0 | 0 | 600 | 600 | 1200 | 150
| 2 | Lights | 20 |  |  |  | 4 | 0 | 0 | 0 | 160 | 160 | 40
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Women Ward | 1 | Light | 20 |  |  |  | 4 | 0 | 0 | 0 | 80 | 80 | 20
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 1 | Computer | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Emergency Room | 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 2 | Lights | 20 |  |  |  | 4 | 0 | 0 | 0 | 160 | 160 | 40
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Vaccine and Blood Draw | 3 | Lights | 20 |  |  |  | 4 | 0 | 0 | 0 | 240 | 240 | 60
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Hallway | 2 | Lights | 20 |  |  |  | 4 | 0 | 0 | 0 | 160 | 160 | 40
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Information Room | 6 | Computers | 75 |  |  | 4 | 4 | 0 | 0 | 1800 | 1800 | 3600 | 450
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 2 | Lights | 20 |  |  | 4 | 4 | 0 | 0 | 160 | 160 | 320 | 40
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Archives | 1 | Light | 20 |  |  | 2 | 2 | 0 | 0 | 40 | 40 | 80 | 20
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Nutrition Room | 1 | Computer | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 2 | Lights | 20 |  |  | 2 | 2 | 0 | 0 | 80 | 80 | 160 | 40
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Pharmacy Office | 1 | Computer | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 1 | Fan | 75 |  |  | 4 | 4 | 0 | 0 | 300 | 300 | 600 | 75
| 1 | Light | 20 |  |  | 4 | 4 | 0 | 0 | 80 | 80 | 160 | 20
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Pharmacy Storage | 4 | Fans | 75 |  |  | 4 | 4 | 0 | 0 | 1200 | 1200 | 2400 | 300
| 2 | Lights | 20 |  |  | 4 | 4 | 0 | 0 | 160 | 160 | 320 | 40
|  | Refrigerator is Gas | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Dorm - Upstairs | 25 | Lights | 20 |  |  |  | 4 | 0 | 0 | 0 | 2000 | 2000 | 500
| 15 | Fans | 75 |  |  |  | 3 | 0 | 0 | 0 | 3375 | 3375 | 1125
| 1 | Refrigerator | 50 |  |  | 4 | 20 | 0 | 0 | 200 | 1000 | 1200 | 50
| 1 | Water Cooler | 30 |  |  | 4 | 20 | 0 | 0 | 120 | 600 | 720 | 30
| 1 | Toaster Oven | 1200 |  |  | 0.5 |  | 0 | 0 | 600 | 0 | 600 | 1200
| 8 | Laptops | 60 |  |  |  | 3 | 0 | 0 | 0 | 1440 | 1440 | 480
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Total | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Total | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0
Grand Totals | [7 empty] | 1440 | 1170 | 25970 | 28955 | 57535 | 12445

## Boucancarre - Additional
SunEnergy Power International
Site Assessment Workbook
Input Information
2008-09-20
Facility Name |  | PIH - Boucancarre
Additional Loads - not for Solar
Hrs per Day
Area | QTY | Load | Watts |  |  | Watthours | Watthours | Watthrs | Total | Days | Wkly
|  |  | Each | Day | Night | Day | Night | Total | Conn | Per Wk | Calc
Watts
Air Conditioners | [5 empty] | 0 | 0 | 0 | 0
Lab | 1 | 24,000 BTU | 2400 | 5 |  | 12000 | 0 | 12000 | 2400
OR | 1 | 18,000 BTU | 1800 | 5 |  | 9000 | 0 | 9000 | 1800
Pharmacy Depot | 1 | 18,000 BTU (planned) | 1800 | 5 |  | 9000 | 0 | 9000 | 1800
Air conditioner load time is based on running 10 hours at 50% duty cycle and an assumed EER of 10. | [5 empty] | 0 | 0 | 0 | 0
Bank | 4 | Computers | 150 | 8 |  | 4800 | 0 | 4800 | 600
| 10 | Lights | 20 | 8 |  | 1600 | 0 | 1600 | 200
| 4 | Fans | 75 | 8 |  | 2400 | 0 | 2400 | 300
| 8 | Receptacles - Misc | 50 | 8 |  | 3200 | 0 | 3200 | 400
| 2 | Printers | 100 | 1 |  | 200 | 0 | 200 | 200
[6 empty] | 0 | 0 | 0 | 0
Restaurants in City | 3 | Refrigerator | 20 | 12 | 12 | 720 | 720 | 1440 | 60
| 6 | Lights | 20 |  | 4 | 0 | 480 | 480 | 120
[6 empty] | 0 | 0 | 0 | 0
Jordan's House | 1 | Refrigerator | 20 | 12 | 12 | 240 | 240 | 480 | 20
| 8 | Lights | 20 |  | 5 | 0 | 800 | 800 | 160
| 2 | Computers | 60 |  | 4 | 0 | 480 | 480 | 120
| 1 | TV | 150 |  | 4 | 0 | 600 | 600 | 150
[6 empty] | 0 | 0 | 0 | 0
Misc. Homes in Village | 20 | Lights - 20W | 20 |  | 4 | 0 | 1600 | 1600 | 400
[6 empty] | 0 | 0 | 0 | 0
Internet Café | 6 | Computers | 150 | 4 | 4 | 3600 | 3600 | 7200 | 900
| 4 | Lights | 40 | 4 | 4 | 640 | 640 | 1280 | 160
| 1 | Satellite Connection | 20 | 12 | 12 | 240 | 240 | 480 | 20
| 2 | Printers | 100 | 1 | 1 | 200 | 200 | 400 | 200
[6 empty] | 0 | 0 | 0 | 0
X-Ray | 1 | Estimate | 1000 | 6 |  | 6000 | 0 | 6000 | 1000
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
Total | [5 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0 |  | 0
Total | [5 empty] | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0
Grand Totals | [5 empty] | 53840 | 9600 | 63440 | 11010

## Sheet2
SunEnergy Power International
Site Assessment Workbook
2008-09-20

## Example System Size
System Size
Haiti Energy Team
Non Sant Sante a: Lopital XXX
Facility | Date of commissioning | Equipment installed |  | Power source |  | Last visited
|  | Inverters | Batteries | Grid | Generator/ Delco
Lopital XXX | 2009-07-07 | 4 Outback inverters VFX-3648 (3 contact and 1 no-contact) | 24 Rolls batteries S-530; 48 V battery bank of 1,200 Ah, 56,000Wh | Yes | 80 KW generator was repaired by PROSER on Feb. 23, 2011 | Feb. 18, 2011
***This design is based on _8__ hours of Delko or EDH each day